	Section Cover Page

	
Section 02 85 16

2024-06-18
Mould Containment Procedures


Use this Section, as applicable, in conjunction with Section 02 85 05 - Mould Removal General Requirements, and Section 02 85 33 - Mould Removal Procedures.

This Section may be used as part of a renovation contract or as part of a contract directly with a hazardous waste disposal contractor.  Edit this Section to suit contracting option selected.

This Technical Specification Section contains:

.1
This Cover Sheet

.2
Specification Section Text:

1.
General

1.1
Intent

1.2
Section Includes

1.3
Related Sections

1.4
Definitions

1.5
Submittals

1.6
Fire Regulations

2.
Products

2.1
Barrier Materials

2.2
Equipment

2.3
Decontamination Facilities

2.4
Negative Pressure Ventilation System

3.
Execution

3.1
HVAC System Isolation

3.2
Electrical System Isolation

3.3
Installation of Barriers

3.4
Removal of Barriers

1.
General

1.1
INTENT

.1
Read this Section in conjunction with Section 02 85 05 - Mould Removal General Requirements.

1.2
SECTION INCLUDES

.1
This Section includes requirements for:

.1
isolation of mould removal containment area from other building spaces [and exterior environment]

.2
measures to maintain airborne mould levels inside and outside of mould removal containment area to acceptable levels, and;
.3
measures to control transfer of materials and personnel in and out of mould removal containment area, to minimize escape of airborne mould from containment area.

1.3
RELATED SECTIONS

.1
Mould Removal General Requirements:
Section 02 85 05.

.2
Mould Removal Procedures:
Section 02 85 33.

1.4
DEFINITIONS

.1
Barrier:  means construction designed to isolate and seal mould removal containment area from remainder of building and from the exterior environment before, during, and after work. 

1.5
SUBMITTALS

.1
Prior to commencement of work on site, submit Mould Removal Plan.  Include following information:

.1
Locations of:

.1
mould removal areas

.2
change rooms

.3
isolation/containment barriers

.4
decontamination facilities

.5
negative air units

.6
exhaust for negative air units

.2
Layout of change rooms.

.3
Sequencing of mould removal related work.

1.6
FIRE REGULATIONS

.1
Comply with requirements of authority having jurisdiction over fire safety, including following:

.1
location of emergency and fire exits from work area.

.2
on-site firefighting equipment.

2.0
Products

2.1
BARRIER MATERIALS

.1
Sheet Material for Walls and Ceilings:  polyethylene, to CAN/CGSB‑51.34‑2022, minimum 150 micrometre thick.

.2
Sheet Material for Floors:  sheet polyethylene, glass fibre reinforced, minimum 250 micrometre thick.

.3
Dimension Board Lumber:  to CAN/CSA‑0141‑23 and graded in accordance with current National Lumber Grades Authority (NLGA) Standard Grading Rules for Canadian Lumber.

.1
Moisture Content:  maximum 19% at time of installation.

.2
Surface Finish:  S4S for members receiving finishes, S2S or S4S for members not receiving finishes.

.4
Wood Panel Products:

.1
Canadian Softwood Plywood:  to CSA 0151-09 (R2014)
.2
Douglas Fir Plywood:  to CSA 0121-08 (R2013)
.3
Poplar Plywood:  to CSA 0153-2013 (R2017)
.4
Waferboard and Oriented Strand Board:  to CSA 0437 Series 93 (R2011)
.5
Tape:  moisture-resistant duct tape.

2.2
EQUIPMENT

.1
Negative Air Units:  two-stage HEPA filter system and accessories required to exhaust air to outside of building.

2.3
DECONTAMINATION FACILITIES

.1
Decontamination facilities shall include:

.1
clean change room

.2
wash station
.3
mould waste transfer rooms

.4
protective equipment storage

.5
toilet facilities (to be assigned by the [Province] [Environmental Consultant])

SPEC NOTE:  If possible and practicable, specify Contractor’s use of existing toilet facilities located outside of mould containment area.  Specify in Division 01.

.2
Provide minimum number of entrances into decontamination facility from outside mould removal containment area.

.3
Obtain [Environmental Consultant] approval of location and construction of decontamination facility prior to commencement of work.

.4
Provide adequate facilities for storage of protective equipment in decontamination facility.

.5
Hot and cold water supply lines shall have water shut‑off valve located outside of mould removal containment area.

2.4
NEGATIVE PRESSURE VENTILATION SYSTEM

.1
Provide negative pressure ventilation system that is separate from building mechanical system.  Confirm leak testing of equipment fitted with HEPA filters after filter installation has been completed with Dioctyl Phthalate (DOP) or equivalent on site.

.2
System shall include:

.1
make‑up air drawn through decontamination facility.

.2
exhaust air vented to building exterior through HEPA filtered negative air units.
.3
System shall:

.1
be capable of changing total volume of air in the containment area five times per hour, and

.2
maintain a negative pressure of at least 5 Pa across barrier between clean area and mould removal containment area.

.4
Start operation of negative air system before beginning wall mould removal work.  Operate continuously until wall mould removal work has been completed, and a visual inspection and surface samples have been taken by the [Environmental Consultant] to verify complete mould removal.

.5
Monitor condition of filters on a regular basis and replace filters as required to maintain air changes and negative pressure.

3.
Execution

3.1
HVAC SYSTEM ISOLATION

.1
Shut down the HVAC system that supplies air within the mould removal containment area.

.2
Seal openings to HVAC system, within the mould removal containment area, to prevent airborne mould from entering system.

.3
Coordinate mechanical system isolation with [Province].

3.2
ELECTRICAL SYSTEM ISOLATION

.1
Isolate electrical systems which will remain energized in mould removal containment area, with ground fault interrupters.

.2
Use only ground fault protected electrical services for electrical equipment used in mould removal containment area.

.3
Coordinate electrical system isolation with [Province].

3.3
INSTALLATION OF BARRIERS

.1
Isolate mould removal containment area from remainder of building.

.2
Seal off openings in perimeter including, but, not limited to, following:

.1
heating and ventilation grills and outlets

.2
doorways

.3
elevator shafts (if applicable)

.4
corridors

.5
openings for lighting and electrical systems

.6
sleeves in ceiling space and floors, above and below work area

.3
Use barrier materials to construct entrances, exits and transfer openings to decontamination area, in an arrangement to form an airlock between doors.  Door arrangement shall meet following criteria:

.1
one door shall always be closed as workers pass through entry system.

.2
under negative pressure, supply air can be drawn in through entry system.

.3
in event of loss of negative pressure, door systems shall seal to prevent airborne fibres from escaping mould containment area.

.4
Seal HVAC supply and return air louvres, [elevator doorways (if applicable)] and grilles to prevent contamination of system.  Cover louvres and grilles with rigid material such as plywood or sheet metal, and seal with two layers of polyethylene.  Obtain [Environmental Consultant] approval prior to using an alternative sealing method.

.5
After penetrations through floors have been sealed, protect floors with one layer of fibre‑reinforced polyethylene.  Seal joints and perimeter with tape.

.6
Protect wall-mounted equipment from mould contamination by sealing with polyethylene.  Where equipment is left exposed, thoroughly clean after completion of mould removal work.

SPEC NOTE:  Specify additional requirements for unique circumstances and conditions.

.7
[                                                                                    ].

3.4
REMOVAL OF BARRIERS

.1
Upon completion of mould removal work, perform following:

.1
Wipe down and spray polyethylene sheets used to protect walls and floor, using mould remediation solution and then spray with sealer.

.2
Remove polyethylene wall sheets after visible inspection approval has been given and after surface samples have been taken by the [Environmental Consultant]. [Environmental Consultant] will advise when to remove sheeting.

.3
Carefully fold sheets with mould exposed side folded in.  Dispose of as mould waste.
.2
Remove other barrier materials from site.
END OF SECTION

	TS Technical Specification
	

	Alberta Infrastructure
Technical Specification System
	Page 0



