PAGE  

	Section Cover Page

	
Section 14 01 24


Hydraulic Elevator Oil Loss Monitoring

2008-06-02
Task and Frequency Schedule


This Master Specification Section contains:

.1
This Cover Sheet

.2
Specification Section Text:

1. Related Sections

2. Requirements

1. Related Sections

.1
Elevator Device Maintenance:
Section 14 01 01

.2
Elevator Task and Frequency Schedule
Section 14 01 22

.3
Preventive Maintenance Log Sheet for Elevators
Section 14 01 23

2. Requirements

.1
Oil loss monitoring shall be implemented for all hydraulic elevators with buried cylinders. Monitoring procedures shall address specific sight conditions for each elevator. As a minimum include the following:

.1
All hydraulic equipment including cylinder heads, platen plates, piping, shut-off valves, control valves, pumps, motors, tanks, and any other component of the hydraulic system or component exposed to hydraulic oil should be kept clean and dry ay all times.

.2
Collect any hydraulic oil that leaks from the hydraulic system.

.3
Seal excessive hydraulic oil leaks.

.4
All collected hydraulic oil shall be filtered and returned to the hydraulic system.  If the oil is contaminated replace with the exact quantity of new oil.

.5
Provide an accurate method of measuring the oil level in the tank. The level shall be measured with the car parked in the same position each time.

.6
The oil level shall be checked on a monthly basis, any loss of oil must be accounted for.

.7
The monthly checks shall be recorded in the logbook. The information recorded shall include as a minimum; 


.1
date


.2
oil level


.3
description of any losses (amount and location)


.4
name and signature of mechanic 

.8
The logbook shall include a detailed description of how to perform the oil loss monitoring tests for each specific elevator.

.9
If oil is added to the system for reasons other than unaccountable oil loss, the addition shall be recorded in the logbook and the new reference point for oil level measurement shall be recorded.

.10
Should unaccountable oil loss be detected or suspected, notify the Minister and arrange for a full load leak-down test. If unaccountable oil loss is confirmed the unit shall be taken out of service until repairs are complete.

END OF SECTION

	PMSMS Property Management Services Master Specification
	

	Alberta Infrastructure
Master Specification System
	Page 0



